Typical Specification

Trident-S Three-Phase Two-way Solid Dielectric Load Break Switch

Part 1-GENERAL

  - DESCRIPTION

The switch shall consist of a solid dielectric insulated manually operated load break switch.

  - QUALITY ASSURANCE

- Manufacturer Qualifications:  The chosen manufacturer shall have at least 10 years experience in manufacturing solid dielectric insulated medium voltage switchgear. The manufacturer shall be completely and solely responsible for the performance of the fault interrupter as rated.

- The manufacturer shall furnish certification of ratings of the load break switch upon request.

- The switch shall comply with requirements of the latest revision of applicable industry standards, including:

IEEE C37.74, ANSI/IEEE 386, IEC60529, IEEE 592

- The switch shall be tested to IEC 60529 for submersibilty.  The switch shall be rated IP68 for 20 days with a 20 foot head of water.

- The switch manufacturer shall be ISO 9001 and 14001 certified.

- The switch shall be RUS approved

  - DELIVERY, STORAGE, AND HANDLING

- The load break switch shall be shipped preassembled at the factory. No field assembly shall be required.

- The contractor, if applicable, shall handle, transfer and move the switches in accordance with manufacturer’s recommendations.

PART 2-PRODUCTS

2.1 SWITCH CONFIGURATION

- The load break switch shall be a two way device

- The load break switch shall be designed for front access to cables and operators

  - SWITCH CONSTRUCTION

- The load break switch shall be a dead-front design.  The operating mechanism housing shall be stainless steel with a viewing window for verification of vacuum interrupter contact position.  The housing shall be painted ANSI 70 light gray using corrosion-resistant epoxy paint.  Operating handles shall be padlockable and adaptable to keylock schemes.  The operating shaft shall be stainless steel providing maximum corrosion resistance. A double "O" ring shaft seal shall be used for a leak resistant, long life seal.

- The solid dielectric module must be coated with a semi-conductive layer of epoxy, providing a completely dead front device.  The semi-conductive layer must be tested to IEEE 592 to ensure it can carry fault current to ground so as to ensure operator safety.

- The load break switch shall be designed for long term operation in the harshest environments.  The interrupter design must be tested to IEC60529 and achieve a protection rating of IP68, subjected to a 20’ head of water pressure for 20 days.

- The load break switch shall interrupt all load currents within the vacuum bottle.

- The load break switch mechanism shall consist of three individual vacuum bottle assemblies mechanically linked to a single spring-assisted operating mechanism.  Manual opening and closing of the load break switch shall be via an operating handle.

2.3 DESIGN RATINGS

Load Break Switches shall be rated

| SELECTION OF RATINGS | IEEE/IEC |  |  |  |
| --- | --- | --- | --- | --- |
| Maximum Design Voltage, kV | 15.5 | 27 | 29.3 | 38 |
| Impulse Level (BIL) Voltage, kV | 110 | 125 | 125 | 150 |
| Continuous Current, Amperes | 800 | 800 | 800 | 800 |
| Load break Current, Amperes | 800 | 800 | 800 | 800 |
| One Minute Withstand (dry), AC kV | 35 | 50 | 50 | 70 |
| Production Test Rating | 34 | 40 | 40 | 50 |
| 15 Minute Withstand, DC kV | 53 | 78 | 78 | 103 |
| Momentary Current, kA, ASYM | 20 | 20 | 20 | 20 |
| Fault-Close Current, kA, ASYM | 20 | 20 | 20 | 20 |
| One Second Current, kA, SYM | 12.5 | 12.5 | 12.5 | 12.5 |
| Mechanical Endurance, Operations | 2000 | 2000 | 2000 | 2000 |

  - CABLE ENTRANCES

Cable entrances shall be tested to IEEE 386 and be, as indicated on the switch drawing:

____600A Apparatus bushing per IEEE 386 figure 11

____200A Bushing wells per IEEE 386 figure 3

2.5 PAD MOUNT ENCLOSURE

Note to specifier: for pad mount applications only

The enclosure shall be fabricated of 12 gauge galvanized steel and manufactured to ANSI C37.72 and C57.12.28 standards.  The enclosure shall be tamper resistant incorporating hinged access doors with pentahead locking bolts and provisions for padlocking. The enclosure shall be provided with lifting provisions and painted with a Munsell 7.0GY3.29/1.5 green finish.

2.6 FACTORY PRODUCTION TESTS

Each load break switch shall undergo the following production testing.  Test reports must be available upon request

- A mechanical operation check

- AC hi-pot tested one minute phase-to-phase, phase-to-ground and across the open contacts

- Circuit resistance shall be checked.

- Each solid dielectric module shall undergo an X-ray inspection and a partial discharge test to ensure void-free construction.

- Leak test to insure the integrity of all seals and gaskets

2.7 STANDARD COMPONENTS

The following shall be included as standard:

- Welded stainless steel mechanism housing painted light gray with stainless steel and brass fasteners.

- Lifting provisions

- ½”-13 nuts to provide sufficient grounding provisions for interrupter and all cable entrances.

- Stainless steel three line diagram and corrosion-resistant nameplates.

- Switch operating handle with padlock provision.

- Removable parking stands

- Mounting bracket

- Operating handle

2.8 OPTIONS

(Choose as necessary for the application)

The following options shall be supplied:

- Mounting frame to bolt switch to the floor (specify galvanized or stainless steel construction.  Specify height of lowest bushing)

- 4/0 brass ground lugs

- Provisions to mount a  key interlock after installation

- Keylock installed at the factory, to lock in open position

- Two (2) Form C contacts for remote monitoring of the position of the vacuum bottle contacts.

- Junction box for wiring Form C contacts or external power source for Electronic Control (specify NEMA 4X for dry applications or NEMA6P for wet/damp applications)

- 12-gauge stainless steel pad mount enclosure manufactured to ANSI C37.72 and C57.12.29 standards.  The enclosure shall be tamper resistant incorporating hinged access doors with pentahead locking bolts and provisions for padlocking. The enclosure shall be provided with lifting provisions and painted with a Munsell 7.0GY3.29/1.5 green finish.

2.9 LABELING

A. Hazard Alerting Signs

The exterior of the pad mount enclosure (if furnished) shall be provided with “Warning--Keep Out--Hazardous Voltage Inside--Can Shock, Burn, or Cause Death” signs. Each unit of switchgear shall be provided with a “Danger--Hazardous Voltage--Failure to Follow These Instructions Will Likely Cause Shock, Burn, or Death” sign. The text shall further indicate that operating personnel must know and obey the employer’s work rules, know the hazards involved, and use proper protective equipment and tools to work on this equipment. Each unit of switchgear shall be provided with a “Danger--Keep Away--Hazardous Voltage--Will Shock, Burn, or Cause Death” sign.

B.  Nameplates, Ratings Labels, and Connection Diagrams

Each unit of switchgear shall be provided with a nameplate indicating the manufacturer’s name, catalog number, model number, date of manufacture, and serial number. Each unit of switchgear shall be provided with a ratings label indicating the following: voltage rating; main bus continuous rating; short-circuit rating; and load break switch ratings including duty-cycle fault-closing and short-time.